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BID PACKAGE BP-12 – ELECTRICAL, FIRE ALARM & LOW VOLTAGE
Scope of Work & Bid Form  |  Pender High School Food & Nutrition Lab Renovation  |  5380 NC-53 West, Burgaw, North Carolina 28425
Construction Manager at Risk: Daniels & Daniels Construction Co., Inc. | Owner: Pender County Schools | Architect: LS3P Associates Ltd. (7201-261295)
Bids due Tuesday, October 20, 2026, 2:00 PM  |  Questions: Erik Barrow, VP of Preconstruction, estimating@danddcc.com, 919-778-4525
	1. SUMMARY AND KEY DATES



Make-safe for demolition, temporary power, new 300A DOAS service, Panel K, power, lighting, fire alarm, and low voltage. Bid per the ITB, the 95% Construction Documents dated September 29, 2026, and all addenda. Bidders must be prequalified.
	Pre-bid meeting
	Mon 10/12, 2:00 PM, Pender HS front office
	Prequalification due
	Wed 10/14, 5:00 PM

	RFIs due
	Wed 10/14, 5:00 PM, estimating@danddcc.com
	Prequalified list / protests
	Thu 10/15 / noon Fri 10/16

	Final addendum
	Thu 10/15
	Bid opening
	Tue 10/20, 2:00 PM, Herring Resource Center, 798 US-117, Burgaw

	Notice to Proceed
	11/3/2026 (anticipated)
	Substantial / Final
	Jan 4 / Jan 15, 2027 (confirm by addendum)


 
	2. SCOPE OF WORK (furnish and install complete, including but not limited to)



· Coordinate electrical demolition with BP-01: de-energize, disconnect and make safe all circuits per E-101, terminate back to source, and mark items safe for removal. BP-01 removes and disposes. BP-12 removes, stores and reinstalls the exit sign and fire alarm devices.
· Temporary power and lighting.
· New 300A service from the utility transformer to the fused DIS-DOAS, with grounding, plaques, trenching and restoration. Coordinate the utility tap and outage; utility charges are by the Owner.
· Panel K with feeder and breaker from existing 2MDP (field verify).
· All branch circuits, receptacles and island pop-ups (including underground conduit), and power wiring with disconnects and starters to all equipment, including DOAS, fans, hoods, WH-1, CP-1 and the gas solenoid.
· Lighting and controls per E-102.
· Fire alarm modifications including the duct detector and fan shutdown, programming and testing.
· TV and data outlets with Cat 6 cabling, WAP relocation, and boxes and raceway for Owner AV.
· Permits, labeling, testing, as-builts and firestopping.
· Fire alarm shop drawings, battery and voltage-drop calculations, and AHJ acceptance testing.
· Alternates: Alt 2 – West wall casework – devices; Alt 3 – South wall casework and sink – devices; Alt 7 – Demonstration station electrical finish.
References: Divisions 26 and 28. Drawings E-001, E-101, E-102. All other sections and sheets as they apply.
 
	3. WORK BY OTHERS AND CLARIFICATIONS



Not included: Removal and disposal of demolished electrical (BP-01); Utility charges and AV equipment (Owner); Slab cutting (BP-01) and pour-back (BP-02); Controls and DDC wiring (BP-11).
· The feeder route is not dimensioned. Price 150 LF underground; the difference is adjusted by unit price.
· Alt 7: the Base Bid includes conduit only at the demonstration station; devices, wiring and connections are Alt 7.
 
	4. GENERAL REQUIREMENTS



· Bid basis: Lump sum, complete and turnkey, including labor, material, equipment, supervision, hoisting, sales tax, permits and fees. This scope sheet assigns work between packages but does not limit it: work shown or specified that is customary to this trade is included.
· Bidding: Bid only on this Bid Form, in a sealed envelope marked with company name, bid package number and the bid opening location. Only exclusions written on the Bid Form are recognized. Bids are valid for 45 days.
· Insurance: WC statutory, EL $1M; CGL $1M/$2M; Auto $1M; Umbrella $1M. Owner and D&D named additional insured, with waiver of subrogation.
· School site: Background checks for all workers, ID worn, and no contact with students; E-Verify required. Noisy work and shutdowns are scheduled through the CM, and premium time is included. Hot work requires a permit and fire watch. Assume lead paint is present (RRP practices required).
· Each trade: Protects existing work and repairs its own damage, works within the dust partitions, cleans up daily, and uses the CM dumpster (BP-01 provides its own). Each trade also does its own layout, firestopping, and cutting and patching, except slab and GWB work assigned above.
· Schedule and closeout: Submittals are due within 10 working days of award. Man the job to the CM schedule, including winter break, and accept pass-through LDs of $500 per day. Provide as-builts, O&M manuals, warranties and training, with a one-year warranty from Substantial Completion.

	BID FORM – BP-12 ELECTRICAL, FIRE ALARM & LOW VOLTAGE



The undersigned, having examined the site and the Bidding Documents, proposes to furnish all labor, materials, equipment and supervision for Bid Package BP-12 – Electrical, Fire Alarm & Low Voltage, Pender High School Food & Nutrition Lab Renovation, in accordance with the drawings, specifications and this scope sheet, for the following amounts:
	Company
	
	NC License No. / Class
	

	Address
	
	Contact / Phone
	

	Email
	
	Prequalified? (Y/N)
	


A. Base Bid (lump sum, 100% turnkey)
	Written in words
	

	Figures
	$


B. Alternates (ADD or DEDUCT; write “No Change” if none)
	No.
	Description
	Amount

	Alt 2
	West wall casework – devices
	Add / Deduct $

	Alt 3
	South wall casework and sink – devices
	Add / Deduct $

	Alt 7
	Demonstration station electrical finish
	Add / Deduct $


C. Requested Pricing
	Description
	Amount

	Deduct if DOAS is fed from existing 2MDP in lieu of new service
	Deduct $


D. Unit Prices (installed, including overhead and profit)
	Description
	Unit
	Unit Price

	300A feeder, underground incl. trench
	LF
	$

	Additional 20A receptacle circuit
	EA
	$

	Additional data drop, Cat 6
	EA
	$


E. Lead Times and Duration
	Item
	Weeks / days
	Notes

	Submittals after award (working days)
	
	

	Material lead time (weeks)
	
	

	On-site duration (working days) / crew size
	
	


F. Bidder’s Exclusions and Qualifications (only items listed here will be recognized)
	


G. Addenda Received
	No.
	
	No.
	
	No.
	
	No.
	


Certification: Bidder accepts the Invitation to Bid and this scope sheet; will honor this bid for 45 days; will comply with the Owner’s background checks, E-Verify and the insurance requirements; and represents that this bid was prepared without collusion (Sherman Act and NC law).
	Authorized Signature
	
	Date
	

	Name / Title
	
	Federal TIN
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